# CROSS FLOW FAN - DC Motor

LWCD-65520LG-06-00

Ningbo Longwell Electric Technology CO.,LTD

NO.100, Ditang District ,Yuyao,Zhejiang Province,China 315400 Phone 86 574 6218 9863

Fax 86 574 6218 9863

sales@zjlongwell.com

www.longwellfans.com

| Model No.: | LWCD-65520LG-06-00 |
| --- | --- |
| Version Number: | A0 |
| Make : | ZHANG |
| Review : | YE |
| Approvd : | GUO |
| Date： | 20260813 |

| Version number | Notes Remarks | Reason content | Revised by | Date |
| --- | --- | --- | --- | --- |

— 1 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

.

Phone: 0086 574 6218 9863        FAX : 0086 574 6218 9863        www.longwellfans .com       sales@zjlongwell.com

LWCD-65520LG-06-00

CROSS FLOW FAN - DC Motor

Nominal Data

| Project1 | Unit | Rating |
| --- | --- | --- |
| Nominal Voltage : | [VDC] | 12 |
| Voltage Range: | [VDC] | 9~16 |
| Speed : | [rpm] | 1800±5% |
| Current : | [A] | 2.7 ±10% |
| Power input : | [W] | / |
| Air flow (Max) : | [m3/h] | 606 |
|  | [CFM] | 357 |
| Static pressure ( Max) : | [Pa] | 52 |
| Noise level : | dB(A) | 53 |
| Max.ambient Temp : | ℃ | 60 |
| Min.ambient Temp : | ℃ | -25 |
| Rotating Direction： |  | CCW |

## Technical Features

| Production Reference Standard | GB12350《 Safety requirements of small power motors》 JB/T10563 《technical specification for general purposes centrifugal fans》 EN60335-1《 Household and similar electrical appliances-safety》 ISO5801-1997《 Industrial fans-performance testing using standardized airways》 GB/T2888《 Methods of Noise Measurement for Fans Blowers Compressors and Roots Blowers》 |
| --- | --- |
| Certification | CE |
| Environmental Protection | RoHS 、Reach |

— 2 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

LWCD-65520LG-06-00

CROSS FLOW FAN - DC Motor

Technical Features

| Service Environment | Operating temperature：-25~60℃；Operating humidity：5 ~ 90 % RH Storing temperature：-25 ~ 60℃；Storing humidity： ≤95 % RH Applicable altitude range：＜1000m |
| --- | --- |
| Life Expectance | 40,000Hours(L10)，At 25℃ room, humidity 15%~65%RH. |
| Balancing | According to JB/T 9101-1999 requirements G6.3 |
| Vibration of The Fan | Test method accord with JB/T 8689 |
| Installation Method | Horizontal or vertical installation |
| Material | Aluminium( Impeller ) The whole machine is electrophoresis |
| Bearing | Maintenance-free deep groove ball bearings |
| Weight | APPROX / (Kg) |

## Electrical Protection

| Speed Control | Control input 0~ 10VDC |
| --- | --- |
| VSP Control | Control signal VSP voltage range1VDC~10VDC (During normal operation, when the VSP voltage is below 1.2VDC, the motor switches from operating mode to standby mode) |
| PWM Control | PWM signal: frequency 1K～10KHz, amplitude 10V,duty cycle 10% ～100% . |
| Signal Output | Tach output：2 Pulse/R；FG internal open circuit output, external pull-up resistor R, pull-up voltage V+ |
| Serial Communication | / |

— 3 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

LWCD-65520LG-06-00

CROSS FLOW FAN - DC Motor

Noise Test

Noise is measured rated voltage in free air in an echoic chamber with B&K sound level meter with microphone at a distance of one meter from the fan intake.The background noise is 18Db(A) max.

— 4 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

# CROSS FLOW FAN - DC Motor

LWCD-65520LG-06-00

## Product Drawing

— 5 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

LWCD-65520LG-06-00

CROSS FLOW FAN - DC Motor

Wiring Diagram

Label

Confirm by sales team when placing sample order or bulk order

— 6 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

LWCD-65520LG-06-00

CROSS FLOW FAN - DC Motor

Warning:

1.Thefanand motormustbeusedwithintheprescribedscopeoftemperatureand humidity otherwiseit willcauseanunexpecteddamage.

2.Fanisnotsetwrongconnection protection ，Providetheright voltageandlinesequenceaccordingto thenameplateotherwiseitwilldamage theproduct.

3. Wiring depends on the wiring diagram and please connect the earth ground if required. We don't suggesttousetheextensioncord .Any wrongconnectionmay cause thedamageof thefan.

4. Be careful when moving the fan and do not take the blades as a handle because it will cause the distortionandchatter.

5.  Connect  the  thermostat  if  required  otherwise  it  would  damage  the  motor  because  of  the  over

temperature.

6. The  length  of the  mounting  screws  shall  not  exceed the  requirement,  otherwise  the fan will  be

damaged.

7.Donot disassemble the fanarbitrarily.It mayhurt thecapacityofwater tightnessand dynamicbalance orcauseotherserious problems.

8.Theover currentprotector isnecessaryincasethedamagefromtheovercurrent.

9.Installthefanasrequired,anyotherinstalling directionwould affecttheservicelifeoftheproduct.

10.Thefan withinletringshouldbeinstalledfollowtherequirementsorit willaffecttheperformance.

11.Usersshoulduse thestandardcablewheninstall thefan otherwiseitwillaffect the watertightness.

12.Thefanshouldkeepawayfrom thechildrenespeciallythebladeandelectricparts .Andthechildren arenotallowedto operatethe fanalone.

13. Do not connect the white signal cable directly to the red signal cable or the external DC power supply.Otherwise,thefanmaybe damaged.T

14.Pleasedonotperform extractionandinsertionoftheconnectorunderrevolutionirrespectiveof poweronandpoweronandpoweroff , andthe fanshouldnottouchormovewhenrunning.

### 15. Do not lift the fan wire when taking the fan, and do not impact the bearing during the handling

process.

16 The version  change  may  not  be  notified,  please  ask  our  company for the  latest  version when

necessary.

17.Please be informed that we are not responsible for any damage or accidents caused by violating aboverulesto installandoperatethefan.

— 8 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD

CROSS FLOW FAN - DC Motor

LWCD-65520LG-06-00

Approval

DATE :

CUSTOMER APPROVAL

CUSTOMER SIGNATURE:

Product Data Confirm :

— 9 — NINGBO LONGWELL ELECTRIC TECHNOLOGY CO.,LTD